## Functional Safety Parameters
Functional Safety Parameter Listing
Craig McIntyre
Rev 0.97 (11.17.2015)
* Focus on Level, Flow, Density, Analytical, Pressure,Temperature measurement subsystems |  |  |  | Calculations reference (derivations versus given) |  |  |  | Unit values below
* Functional safety parameters are presented as given from the documents and versions referenced
* Parameters that are typically used to derive other parameters are referenced as calculations |  |  |  | λd = λdd+λdu |  | All devices type B |  | λ in FIT = Failure in Time (per billion)
* Application, environmental, operation and lifecycle management guidelines that define the scope and limit conditions for use of these parameters are given in the associated Functional Safety Manuals |  |  |  | λdd = λd*Ca |  | Ca = λdd/ λd |  | TI = Proof (Manual) test intervals (years)
* Proof test coverage is determined by choice of proof testing proceedures (i.e. Full, Partial, Insitu) as defined in the associated Functional Safety Manual |  |  |  | λdu = λd*(1-Ca)*Cm |  | Cm = λdu/( λd*(1-Ca)) |  | MTTR = mean time to restore (hours)
Measurement type/function | Model number(s) | Description | Functional Safety Manual/Version - link to FS qualifying detail, recommendations and options | λsd (safe detected) given | λsu (safe undetected) given | λdd (dangerous detected) given | λdu (dangerous undetected) given | Dangerous failures (λd = λdu + λdd) | Safe failures (λs = λsu + λsd) | SFF (safe failure fraction) given | HFT (hardware fault tolerence) | MTTR mean time to restore | Ca/DC (diagnostic coverage - automatic) calculated. Reference FS manual for detail | Cm/PTC (diagnostic/proof test coverage - manual) calculated Reference PTC details in FS manual | PFD-average with given proof test interval TI | Proof test interval TI | SIL capability | Safety Function | Output(s) | Manufacturer | Class
Loop powered Guided Wave Radar level | FMP50/51/52/53/54/55/56/57 | Levelflex | SD00326F/00/EN/17.15 71281221 | 15 | 608 | 2295 | 199 | 2494 | 623 | 93% | 0 | 8 | 92.02% | 100% | 8,91 x 10-4 | 1 | SIL 2 (single-channel architecture 1oo1), SIL 3 (multi-channel architecture, also with homogeneous redundancy, e.g. 1oo2, 2oo3) | Min,Max, Range | Analog | Endress+Hauser | B
Loop powered Vortex flow | 7C2B (Prowirl C 200) 7D2B (Prowirl D 200) 7F2B (Prowirl F 200) 7O2B (Prowirl O 200) 7R2B (Prowirl R 200) | Prowirl 200-Option A "4-20mA HART" | SD01162D/06/EN/03.15 71291784 | 381 | 651 | 1588 | 87 | 1675 | 1032 | 97% |  |  | 94.81% | 100% | 3.8 · 10-4 | 1 | Use for volume flow monitoring up to SIL 2 (single-channel architecture) or SIL 3 (multi-channel architecture with homogeneous redundancy | Min,Max, Range | Analog | Endress+Hauser | B
Loop powered Vortex flow | 7C2B (Prowirl C 200) 7D2B (Prowirl D 200) 7F2B (Prowirl F 200) 7O2B (Prowirl O 200) 7R2B (Prowirl R 200) | Prowirl 200-Option B "4-20mA HART, pul./freq./switch output" | SD01162D/06/EN/03.15 71291784 | 381 | 659 | 1588 | 87 | 1675 | 1040 | 97% |  |  | 94.81% | 100% | 3.8 · 10-4 | 1 | Use for volume flow monitoring up to SIL 2 (single-channel architecture) or SIL 3 (multi-channel architecture with homogeneous redundancy | Min,Max, Range | Analog/pulse/Frequency/switch | Endress+Hauser | B
Loop powered Vortex flow | 7C2B (Prowirl C 200) 7D2B (Prowirl D 200) 7F2B (Prowirl F 200) 7O2B (Prowirl O 200) 7R2B (Prowirl R 200) | Prowirl 200-Option C "4-20mA HART, 4-20mA" | SD01162D/06/EN/03.15 71291784 | 381 | 1266 | 1413 | 70 | 1483 | 1647 | 98% |  |  | 95.28% | 100% | 3.1 · 10-4 | 1 | Use for volume flow monitoring up to SIL 2 (single-channel architecture) or SIL 3 (multi-channel architecture with homogeneous redundancy | Min,Max, Range | Analog | Endress+Hauser | B
Loop powered Magnetic flow | 5H2B (Promag H 200) 5P2B (Promag P 200) | Option A "4-20mA HART"; Option B "4-20mA HART, pulse/freqency/switch output" | SD01451D/06/EN/01.15 71281909 | 1051 | 608 | 1574 | 156 | 1730 | 1659 | 95% | 0 to 1 |  | 90.98% | 100% | 6.81 · 10-4 | 1 | Use for volume flow monitoring up to SIL 2 (single-channel architecture) or SIL 3 (multi-channel architecture with homogeneous redundancy) | Min. Max, Range | Analog/pulse/Frequency/switch | Endress+Hauser | B
Coriolis mass flow/Density | 80/83 | Promass 80 /83 Catergory 1 (Page 11-13) | SD00077D/06/EN/14.14 71272498 | 0 | 316 | 1214 | 178 | 1392 | 316 | 89.5% | 0 | 8 | 87.21% | 100% | 7.83 · 10–4 | 1 | architecture) or SIL 3 (multi-channel architecture with | Min,Max, Range |  | Endress+Hauser | B
Coriolis mass flow/Density | 80/83 | Promass 80 /83 Catergory 2 ( Page 11-13) | SD00077D/06/EN/14.14 71272498 | 0 | 329 | 1292 | 158 | 1450 | 329 | 91.1% | 0 | 8 | 89.1% | 100% | 6.92 · 10–4 | 1 | homogeneous redundancy) | Min,Max, Range |  | Endress+Hauser | B
Coriolis mass flow/Density | 80/83 | Promass 80 /83 Catergory 3 ( Page 11-13) | SD00077D/06/EN/14.14 71272498 | 0 | 323 | 1221 | 178 | 1399 | 89.6 | 89.6% | 0 | 8 | 87.28% | 100% | 7.83 · 10–4 | 1 | Sil 2 single channel Sil 3 redundant | Min,Max, Range |  | Endress+Hauser | B
Coriolis mass flow/Density | 80/83 | Promass 80 /83 Catergory 4 ( Page 11-13) | SD00077D/06/EN/14.14 71272498 | 0 | 336 | 1300 | 158 | 1458 | 336 | 91.2% | 0 | 8 | 89.16% | 100% | 6.92 · 10–4 | 1 | Sil 2 single channel Sil 3 redundant | Min,Max, Range |  | Endress+Hauser | B
Coriolis mass flow/Density | 80/83 | Promass 80 /83 Catergory 5 ( Page 11-13) | SD00077D/06/EN/14.14 71272498 | 0 | 333 | 1278 | 179 | 1457 | 333 | 90% | 0 | 8 | 87.71% | 100% | 7.87 · 10–4 | 1 | Sil 2 single channel Sil 3 redundant | Min,Max, Range |  | Endress+Hauser | B
Coriolis mass flow/Density | 80/83 | Promass 80 /83 Catergory 6 ( Page 11-13) | SD00077D/06/EN/14.14 71272498 | 0 | 346 | 1356 | 159 | 1515 | 346 | 91.5% | 0 | 8 | 89.5% | 100% | 6.96 · 10–4 | 1 | Sil 2 single channel Sil 3 redundant | Min,Max, Range |  | Endress+Hauser | B
Coriolis mass flow/Density | 80/83 | Promass 80 /83 Catergory 7 ( Page 11-13) | SD00077D/06/EN/14.14 71272498 | 0 | 435 | 1382 | 167 | 1549 | 435 | 91.6% | 0 | 8 | 89.22% | 100% | 7.31 · 10–4 | 1 | Sil 2 single channel Sil 3 redundant | Min,Max, Range |  | Endress+Hauser | B
Coriolis mass flow/Density | 80/83 | Promass 80 /83 Catergory 8 ( Page 11-13) | SD00077D/06/EN/14.14 71272498 | 0 | 351 | 1376 | 160 | 1536 | 351 | 91.6% | 0 | 8 | 89.58% | 100% | 6.99 · 10–4 | 1 | Sil 2 single channel Sil 3 redundant | Min,Max, Range |  | Endress+Hauser | B
Coriolis mass flow/Density | 80/83 | Promass 80 /83 Catergory 9 ( Page 11-13) | SD00077D/06/EN/14.14 71272498 | 0 | 412 | 1384 | 159 | 1543 | 412 | 91.9% | 0 | 8 | 89.7% | 100% | 6.94 · 10–4 | 1 | Sil 2 single channel Sil 3 redundant | Min,Max, Range |  | Endress+Hauser | B
Coriolis mass flow/Density | 80/83 | Promass 80 /83 Catergory 10 ( Page 11-13) | SD00077D/06/EN/14.14 71272498 | 0 | 350 | 1374 | 159 | 1533 | 350 | 91.6% | 0 | 8 | 89.63% | 100% | 6.94 · 10–4 | 1 | Sil 2 single channel Sil 3 redundant | Min,Max, Range |  | Endress+Hauser | B
Coriolis mass flow/Density | Promass 200 | Option A Option A "4-20mA HART" | SD00147D/06/EN/06.15 71283625 | 1374 | 1105 | 1168 | 89 | 1257 | 2479 | 97% |  |  | 92.92% | 100% | 3.9 · 10-4 | 1 | Use for flow monitoring up to SIL 2 (single-channel architecture) or SIL 3 (multi-channel architecture with homogeneous redundancy | Min,Max, Range |  | Endress+Hauser | B
Loop powered Coriolis mass flow/Density | Promass 200 | Option B "4-20mA HART, pulse/frequency/switch output" | SD00147D/06/EN/06.15 71283625 | 1374 | 1105 | 1168 | 89 | 1257 | 2479 | 97% |  |  | 92.92% | 100% | 3.9 · 10-4 | 1 | Use for flow monitoring up to SIL 2 (single-channel architecture) or SIL 3 (multi-channel architecture with homogeneous redundancy | Min,Max, Range |  | Endress+Hauser | B
Loop powered Coriolis mass flow/Density | Promass 200 | Option C "4-20mA HART, 4-20mA" | SD00147D/06/EN/06.15 71283625 | 1374 | 1720 | 1010 | 73 | 1083 | 3094 | 98 |  |  | 93.26% | 100% | 3.2 · 10-4 | 1 | Use for flow monitoring up to SIL 2 (single-channel architecture) or SIL 3 (multi-channel architecture with homogeneous redundancy | Min,Max, Range |  | Endress+Hauser | B
Loop Powered Liquid Analysis | CM42 | Liquiline M CM42 transmitter 4-20mA | SD00153CEN 1310pdf Version 2 | 688 | 947 | 2667 | 236 | 2903 | 1635 | 94.8% | 0 | 8 | 91.87% | 100% | 1.03 × 10-3 | 1 | Hardware: 2, Software: 2 in homogenous redundancy: 2 |  | Analog | Endress+Hauser | B
Liquid Analysis | KSG2-SIL pH | pH Sensor head | SD00161C/00/A2/01.11 | 0 | 630 | 1660 | 190 | 1850 | 630 | 92.3% | 0 | 8 | 89.73% | 100% | 0.83 × 10–3 | 1 | 2 |  |  | Endress+Hauser | B
Liquid Analysis | CKY10 | Cable | SD00162C/00/A2/01.11 | 0 | 630 | 1660 | 190 | 1850 | 630 | 93.3% | 0 | 8 | 89.73% | 100% | 8.31 × 10-4 | 1 | 2 |  |  | Endress+Hauser | B
Loop powered Free space radar level | FMR23x | Micropilot with display | SD150F/00/en/03.04 52016606 | 87 | 1340 | 882 | 766 | 1648 | 1427 | >75% | 0 1) single use |  | 53.52% | 100% | 0,335 x 10-2 | 1 | 2 |  | Analog | Endress+Hauser | B
Loop powered Free space radar level | FMR23x | Mircropilot /without display | SD150F/00/en/03.04 52016606 | 87 | 1150 | 882 | 689 | 1571 | 1237 | >75% | 0 1) single use |  | 56.14% | 100% | 0,263 X10-2 | 1 | 2 |  | Analog | Endress+Hauser | B
Loop powered Free space radar level | FMR 24x | Micropilot with display | SD150F/00/en/03.04 52016606 | 87 | 1340 | 850 | 680 | 1530 | 1427 | >76% | 0 1) single use |  | 55.56% | 100% | 0,297X10-2 | 1 | 2 |  | Analog | Endress+Hauser | B
Loop powered Free space radar level | FMR24x | Mircropilot /without display | SD150F/00/en/03.04 52016606 | 87 | 1150 | 850 | 603 | 1453 | 1237 | >77% | 0 1) single use |  | 58.5% | 100% | 0,263X10-2 | 1 | 2 |  | Analog | Endress+Hauser | B
Loop powered Free space radar level | FMR50/51/52/53/54/56/57 | Micropliot | SD01087F/00/EN/02.15 71281219 | 15 | 520 | 2438 | 245 | 2683 | 535 | 92% | 0 | 8 | 90.87% | 100% | 1.09 × 10–3 | 1 | SIL 2 (single-channel architecture 1oo1), SIL 3 (multi-channel architecture, also with homogeneous redundancy, e.g. 1oo2, 2oo3) | Min,Max, Range | Analog | Endress+Hauser | B
Loop powered Capacitance levelswitch | FTI51/52, FTI55/56, FTI77 | Liquicap/Solicap M /Min Safety | SD278F/00/en/10.08 71078014 | 2 | 334 | 187 | 43 | 230 | 336 | 92% | 0 | 8 | 81.3% | 100% | 1.85X10-4 | 1 | 2 (single-channel), 3 (with use of a SIL 3 capable coincidence logic), → See p18, "Appendix" | Min | Analog | Endress+Hauser | B
Loop powered Capacitance levelswtch | FTI51/52, FTI55/56, FTI77 | Liquicap/Solicap M /Max Safety | SD278F/00/en/10.08 71078014 | 1 | 341 | 188 | 34 | 222 | 342 | 94% | 0 | 8 | 84.68% | 100% | 1.46 x 10-4 | 1 | 2 (single-channel), 3 (with use of a SIL 3 capable coincidence logic), → See p18, "Appendix" | Max | Analog | Endress+Hauser | B
Loop powered Capacitance level | FMI51, FMI52 | Liquicap M | SD00198F/00/EN/13.11 71131920 | 0 | 118 | 695 | 75 | 770 | 118 | 91% | 0 (single channel use) | 8 | 90.26% | 100% | 3,29 × 10 -4 | 1 | 2 | Min,Max | Analog | Endress+Hauser | B
Liquids vibronic Remote switching support unit subsystems | FTL325P | Liquiphant M/S FTL5x(H), FTL51C, FTL7x + Nivotester FTL325P (1oo1D 1oo2D, 2oo3D subsystems) | SD111F/00/en/08.06 52010553 |  |  |  |  | 0 | 0 |  | 0 to 1 | 8 | #DIV/0! | #DIV/0! |  | 1 | 2015-02-03 | Max |  | Endress+Hauser | B
Liquids vibronic detection (i.e. Min point level,empty pipe detection) | FTL 5X,7X insert FEL55 | Liquiphant | SD279F/00/en/06.08 | 54 | 220 | 47 | 86 | 133 | 274 | 78% | 0 | 8 | 35.34% | 100% | 3.76 × 10–4 | 1 | 2 | Min | Analog | Endress+Hauser | B
Liquids vibronic detection (i.e. High point level, overfill protection) | FTL 5X,7X insert FEL55 | Liquiphant | SD 167F/00/en/10.03 52018925 | 79 | 230 | 62 | 72 | 134 | 309 | >83.8 | 0 | 8 | 46.27% | 100% | 0.03 × 10–2 | 1 | 2 | Max | Analog | Endress+Hauser | B
Solids vibronic detection (i.e. High point level, overfill protection)) | FTM50, FTM51, FTM52 | Soliphant | SD208F/00/en/01.06 | 22 | 511 | 161 | 31 | 192 | 533 | 95% | 0 | 8 | 83.85% | 100% | 0.013 × 10–2 | 1 | 2 | Max | Analog | Endress+Hauser | B
Temperature | TMT122 | itemp TMT122 Din Rail Hart-low level | SD007R/09/en/12.05 FM+SGML 6.0 ProMoDo | 26 | 190 | 132 | 110 | 242 | 216 | > 75 % | 0 (single channel use) |  | 54.55% | 100% | 0.000482 | 1 | 2 | Min | Analog | Endress+Hauser | B
Temperature | TMT122 | itemp TMT122 Din Rail HART High Level | SD007R/09/en/12.05 FM+SGML 6.0 ProMoDo | 124 | 190 | 33 | 110 | 143 | 314 | > 75 % | 0 (single channel use) |  | 23.08% | 100% | 0.000482 | 1 | 2 | Max | Analog | Endress+Hauser | B
Temperature | TMT122 | itemp TMT122 Din Rail HART-range | SD007R/09/en/12.05 FM+SGML 6.0 ProMoDo | 141 | 190 | 17 | 110 | 127 | 331 | > 75 % | 0 (single channel use) |  | 13.39% | 100% | 0.000482 | 1 | 2 | Range | Analog | Endress+Hauser | B
Temperature | TMT182 | itemp TMT182 Field transmitter HART low level | SD006R/09/en/12.05 FM+SGML 6.0 ProMoDo | 26 | 165 | 108 | 107 | 215 | 191 | > 73% | 0 (single channel use) |  | 50.23% | 100% | 0.000469 | 1 | 2 | Min | Analog | Endress+Hauser | B
Temperature | TMT182 | itemp TMT182 Field transmitter Hart -High Level | SD006R/09/en/12.05 FM+SGML 6.0 ProMoDo | 101 | 165 | 33 | 107 | 140 | 266 | > 73% | 0 (single channel use) |  | 23.57% | 100% | 0.000469 | 1 | 2 | Max | Analog | Endress+Hauser | B
Temperature | TMT182 | itemp TMT182 Field transmitter Hart-Range | SD006R/09/en/12.05 FM+SGML 6.0 ProMoDo | 117 | 165 | 17 | 107 | 124 | 282 | > 73% | 0 (single channel use) |  | 13.71% | 100% | 0.000469 | 1 | 2 | Range | Analog | Endress+Hauser | B
Pressure | PMP71/75 | Cerabar S | SD00190P/00/EN/14.13 71251400 | 52 | 313 | 396 | 65 | 461 | 365 | 92 | With redundant connection with HFT = 1 (e.g. 1oo2 or 2oo3), the Cerabar S meets SIL3 |  | 85.9% | 100% | 2.86 × 10-4 | 1 | 2 (single-channel), 3 (with use of a SIL 3 capable coincidence logic) | Min | Analog | Endress+Hauser | B
Pressure | PMP71/75 | Cerabar S | SD00190P/00/EN/14.13 71251400 | 396 | 313 | 52 | 65 | 117 | 709 | 92 | With redundant connection with HFT = 1 (e.g. 1oo2 or 2oo3), the Cerabar S meets SIL3 |  | 44.44% | 100% | 2.86 × 10-4 | 1 | 2 (single-channel), 3 (with use of a SIL 3 capable coincidence logic) | Max | Analog | Endress+Hauser | B
Pressure | PMP71/75 | Cerabar S | SD00190P/00/EN/14.13 71251400 | 448 | 313 | 0 | 65 | 65 | 761 | 92 | With redundant connection with HFT = 1 (e.g. 1oo2 or 2oo3), the Cerabar S meets SIL3 |  | 0% | 100% | 2.86 × 10-4 | 1 | 2 (single-channel), 3 (with use of a SIL 3 capable coincidence logic) | Range | Analog | Endress+Hauser | B
Pressure | PMC 71 | Cerabar S Ceramic | SD00190P/00/EN/14.13 71251400 | 52 | 450 | 443 | 85 | 528 | 502 | 91.7 | With redundant connection with HFT = 1 (e.g. 1oo2 or 2oo3), the Cerabar S meets SIL3 |  | 83.9% | 100% | 3.70 × 10-4 | 1 | 2 (single-channel), 3 (with use of a SIL 3 capable coincidence logic) | Range | Analog | Endress+Hauser | B
Pressure | PMC 71 | Cerabar S Ceramic | SD00190P/00/EN/14.13 71251400 | 443 | 450 | 52 | 85 | 137 | 893 | 91.7 | With redundant connection with HFT = 1 (e.g. 1oo2 or 2oo3), the Cerabar S meets SIL3 |  | 37.96% | 100% | 3.70 × 10-4 | 1 | 2 (single-channel), 3 (with use of a SIL 3 capable coincidence logic) | Range | Analog | Endress+Hauser | B
Pressure | PMC 71 | Cerabar S Ceramic | SD00190P/00/EN/14.13 71251400 | 495 | 450 | 0 | 85 | 85 | 945 | 91.7 | With redundant connection with HFT = 1 (e.g. 1oo2 or 2oo3), the Cerabar S meets SIL3 |  | 0% | 100% | 3.70 × 10-4 | 1 | 2 (single-channel), 3 (with use of a SIL 3 capable coincidence logic) | Range | Analog | Endress+Hauser | B
Differential pressure | FMD77, FMD78, PMD75 | Deltabar S | SD00189P/00/EN/14.13 71247245 | 52 | 175 | 876 | 57 | 933 | 227 | 95 | With redundant connection with HFT = 1 (e.g. coincidence logic 1oo2 or 2oo3), the Deltabar S meets the requirements for SIL 3. |  | 93.89% | 100% | 3.02 × 10-4 | 1 | 2 (single-channel); 3 (with use of a SIL 3 capable coincidence logic) | Min | Analog | Endress+Hauser | B
Differential pressure | FMD77, FMD78, PMD75 | Deltabar S | SD00189P/00/EN/14.13 71247245 | 876 | 175 | 52 | 57 | 109 | 1051 | 95 | With redundant connection with HFT = 1 (e.g. coincidence logic 1oo2 or 2oo3), the Deltabar S meets the requirements for SIL 3. |  | 47.71% | 100% | 3.02 × 10-4 | 1 | 2 (single-channel); 3 (with use of a SIL 3 capable coincidence logic) | Max | Analog | Endress+Hauser | B
Differential pressure | FMD77, FMD78, PMD75 | Deltabar S | SD00189P/00/EN/14.13 71247245 | 928 | 175 | 0 | 57 | 57 | 1103 | 95 | With redundant connection with HFT = 1 (e.g. coincidence logic 1oo2 or 2oo3), the Deltabar S meets the requirements for SIL 3. |  | 0% | 100% | 3.02 × 10-4 | 1 | 2 (single-channel); 3 (with use of a SIL 3 capable coincidence logic) | Range | Analog | Endress+Hauser | B
Differential pressure | FMD76, PMD70 | Deltabar S | SD00189P/00/EN/14.13 71247245 | 52 | 175 | 876 | 57 | 933 | 227 | 95 | With redundant connection with HFT = 1 (e.g. coincidence logic 1oo2 or 2oo3), the Deltabar S meets the requirements for SIL 3. |  | 93.89% | 100% | 2.51 × 10-4 | 1 | 2 (single-channel); 3 (with use of a SIL 3 capable coincidence logic) | Min | Analog | Endress+Hauser | B
Differential pressure | FMD76, PMD70 | Deltabar S | SD00189P/00/EN/14.13 71247245 | 876 | 175 | 52 | 57 | 109 | 1051 | 95 | With redundant connection with HFT = 1 (e.g. coincidence logic 1oo2 or 2oo3), the Deltabar S meets the requirements for SIL 3. |  | 47.71% | 100% | 2.51 × 10-4 | 1 | 2 (single-channel); 3 (with use of a SIL 3 capable coincidence logic) | Max | Analog | Endress+Hauser | B
Differential pressure | FMD76, PMD70 | Deltabar S | SD00189P/00/EN/14.13 71247245 | 928 | 175 | 0 | 57 | 57 | 1103 | 95 | With redundant connection with HFT = 1 (e.g. coincidence logic 1oo2 or 2oo3), the Deltabar S meets the requirements for SIL 3. |  | 0% | 100% | 2.51 × 10-4 | 1 | 2 (single-channel); 3 (with use of a SIL 3 capable coincidence logic) | Range | Analog | Endress+Hauser | B
Gamma (i.e. high point level) | FMG60 | Gammapilot M | SD00230F/00/EN/13.11 | 577 | 94 | 1316 | 92 | 1408 | 671 | 96 | 0 | 8 | 93.47% | 100% | 4.04 × 10-4 | 1 | 2/3 | Max | Analog | Endress+Hauser | B
Gamma (i.e. low level) | FMG60 | Gammapilot M | SD00324F/00/EN/02.15 | 344 | 15 | 1638 | 96 | 1734 | 359 | 96 | 0/1 | 8 | 94.46% | 100% | 4.21 × 10-4 | 1 |  | Min | Anaolg | Endress+Hauser | B