SECTION 40 72 33

GUIDED RADAR LEVEL METERS for LIQUIDS

- PART 1-GENERAL

- A. 	Levelflex FMP51 for level measurement even under extreme process conditions like high temperature and high pressure in the process industry. FMP51 offers maximum reliability even in case of moved surface and foam or when numerous tank baffles interfere with the measurement. Levelflex FMP51 is used for continuous level measurement of liquids, pastes and slurries but also for interface measurement. The measurement is not affected by changing media, temperature changes, gas blankets or vapors.

B. 	1.02 SUBMITTALS

- Furnish complete Product Manufacturer’s Technical Information, Operating and Maintenance Manuals

- Product Data:

  - Dimensional Drawings.

  - Materials of Construction:

    - Transmitter Housing

    - Flanges / Process Connection

    - Wetted Components

  - Measurement accuracy.

  - Range and range ability.

  - Enclosure Rating.

  - Classification Rating.

  - Power:

    - Voltage.

    - Wattage.

  - Output options.

1.03 QUALITY ASSURANCE

- Manufacturer’s instruments facilities certified to the quality standards of ISO Standard 9001 - Quality Systems - Model for Quality Assurance in Design/Development, Production, Installation, and Servicing.

1.04 DELIVERY, STORAGE, AND HANDLING

- Store all instruments in a dedicated structure with space conditioning to meet the recommended storage requirements provided by the Manufacturer.

- Any instruments that are not stored in strict conformance with the Manufacturer’s recommendation shall be replaced.

1.05 PROJECT OR SITE CONDITIONS

- Provide instruments suitable for the installed site conditions including, but not limited to, material compatibility, process and ambient temperature, and humidity conditions.

1.06 WARRANTY

- The meter shall have standard one year warranty from date of shipment and if the meter is commissioned by a factory certified technician, the warranty is extended to three years from the date of shipment.

- 1.07 MAINTENANCE

A.          Provide all parts, necessary for maintenance and calibration purposes throughout the warranty period. Deliver all of these supplies before project substantial completion.

1.08 LIFECYCLE MANAGEMENT

A.	Instrument documentation, like original calibration certificates, manuals and product status information shall be accessed via a web enabled system with a license. The instrument-specific information shall be accessed via its serial number. When services are provided by an authorized service provider the services information like subsequent field calibrations shall be archived and accessible via this web enabled system.

PART 2-PRODUCTS

2.01 MANUFACTURER

A. 	Endress+Hauser- Levelflex M FMP51/52/54

2.02 MANUFACTURED UNITS

    - The transmitter housing shall have dual compartments and be available in plastic, die cast aluminum with a powder Epoxy coating or 316L Stainless steel based on the application environment.

    - The transmitter shall be available as a loop powered 2 wire device with an option for 4 wires.

    - The instrument shall be capable of handling process temperatures between -4 degrees F and 392 degrees F. It should also withstand process pressures of -14.5 psi to 580 psi. A high temp / high pressure option shall be available for process temperatures between -321 degrees F and 842 degrees F; process pressure capability from -14.5 to 5800 PSI. The high temp / high pressure instrument shall also have the option for dynamic gas phase compensation to ensure reliable operation.

    - Unit shall have ATEX, FM, CSA or IECEx approvals as required.

    - HART with 4 to 20 mA analog output, Profibus PA, Fieldbus Foundation and a second 4-20mA only output shall be available for system integration.

    - Application in safety related systems with requirements for functional safety up to SIL 3 independently assessed by TUV as per IEC 61508.

    - 316L Stainless steel probe available for lengths up to 13’. 316 steel rope probe available for lengths > 13’ up to a maximum length of 148’. 316L or AlloyC coaxial probes available for ranges up to 20’. A PFA coated probe shall be available for aggressive liquids

    - Unit shall employ multi echo tracking algorithms for reliable level measurement.

    - Process connection shall be available as a NPT or ANSI flange.

    - Unit shall have a maximum error of + or – 2 mm on measuring ranges of less than 49 feet.

    - Unit shall have easy remote operation, diagnosis and measuring point documentation with the supplied operating program; An optional remote display and operation shall be available if required.

    - The transmitter shall have local indicator with a 4-line LCD display scaled to read in engineering units of level and volume. The local indicator shall be capable of displaying an envelope curve of the actual signal used for commissioning / troubleshooting purposes.

    - The display module shall be capable of data backup, data comparison and data transfer functions.

    - Complete set-up and configuration shall be possible via the 3-buttons built-in the display. No further equipment or parts shall be required for commissioning the unit.

    - FDT based software shall be provided for optional remote method of configuration, set-up and storage of parameters via a computer.

    - The transmitter shall have a built-in HistoRom which will store the configuration data and be capable of logging 20 events based on programmed triggers.

- 2.03  	ACCESSORIES

- A Certificate of Compliance shall be available from the manufacturer if required.

- An application data sheet should be filled out with all known data, and submitted to the manufacturer to ensure proper instrument choice. .

2.04 SOURCE QUALITY CONTROL & CALIBRATION

- A.	 Certificate of Compliance shall be available from the manufacturer if required.

- B.	An application data sheet should be filled out with all known data, and submitted to the manufacturer to ensure proper instrument choice. .

2.05 SAFETY

A.	All electrical equipment shall meet the requirements of ANSI/NFPA 70, NATIONAL ELECTRIC CODE, latest addition.

B.	All devices shall be capable of being certified for use in hazardous areas: Class I, II, III, Div. 2, Groups A-G.

C.	All devices shall be suitable for use as non-incendive devices when used with appropriate non-incendive associated equipment.  Devices with intrinsically safe ratings will normally be acceptable with vendor’s approval.

D.	Transmitter housing shall conform to NEMA 4x classification.

E.	Non-intrinsically safe electrical equipment shall be approved by a Nationally Recognized Testing Laboratory (NRTL) such as FM, UL, ETL, CSA, etc. for the specified electrical area classification.

- F.	Electrical equipment specified as intrinsically safe shall qualify as “simple apparatus” or NTRL approved intrinsically safe equipment per ANSI/ISA-RP12.6 “Installation of Intrinsically Safe Systems for Hazardous (Classified) Locations”, latest edition.

PART 3-EXECUTION

- 3.01 EXAMINATION

- Examine the complete set of plans, the process fluids, pressures, and temperatures and furnish instruments that are compatible with installed process condition.

- Examine the installation location for the instrument and verify that the instrument will work properly when installed.

- 3.02 INSTALLATION

- As shown on installation details and mechanical Drawings.

- As recommended by the manufacturer’s installation and operation manual.

- Specific attention should be given to the following technical requirements:

    - Verify the transmitter is mounted in an appropriate location in the vessel as per the instruction manual.

- 3.03 FIELD QUALITY CONTROL

- Demonstrate the performance of all instruments to the ENGINEER before commissioning.

- ENGINEER to witness all instrument calibration verification in the field.

- Each instrument shall be tested before commissioning and the ENGINEER shall witness the response in the PLC control system and associated registers.

- Manufacturer’s Field Services:

- Manufacturers shall be capable of providing complete setup, commissioning and verification of the instrument prior to start up.

- Notify the ENGINEER in writing of any problems or discrepancies and proposed solutions.

- 3.04 ADJUSTING

- Factory calibration of all instruments shall be provided and only commissioning or set-up of parameters shall be required in the field in accordance with the Manufacturer’s instructions.

- 3.05 PROTECTION

- All instruments shall be fully protected after installation and before commissioning.

- Replace any instruments damaged before commissioning:

- The ENGINEER shall be the sole party responsible for determining the corrective measures.