SECTION 40 72 23/33

DUAL TECHNOLOGY (GUIDED RADAR / CAPACITANCE) LEVEL MEASUREMENT SYSTEM

- PART 1	GENERAL

  - SUMMARY

- Levelflex FMP55 guided radar with SensorFusion offers the worldwide first combination of the capacitance and guided radar measuring principle in one device. The instrument guarantees safe measured value acquisition even in emulsion layers and issues level and interface layer signals simultaneously.

1.02 SUBMITTALS

- Furnish complete Product Manufacturer’s Technical Information, Operating and Maintenance Manuals

- Product Data:

  - Dimensional Drawings.

  - Materials of Construction:

    - Transmitter Housing

    - Flanges / Process Connection

    - Wetted Components

  - Measurement accuracy.

  - Range and range ability.

  - Enclosure Rating.

  - Classification Rating.

  - Power:

    - Voltage.

    - Wattage.

  - Output options.

1.03 QUALITY ASSURANCE

- Manufacturer’s instruments facilities certified to the quality standards of ISO Standard 9001 - Quality Systems - Model for Quality Assurance in Design/Development, Production, Installation, and Servicing.

1.04 DELIVERY, STORAGE, AND HANDLING

- Store all instruments in a dedicated structure with space conditioning to meet the recommended storage requirements provided by the Manufacturer.

- Any instruments that are not stored in strict conformance with the Manufacturer’s recommendation shall be replaced.

1.05 PROJECT OR SITE CONDITIONS

- Provide instruments suitable for the installed site conditions including, but not limited to, material compatibility, process and ambient temperature, and humidity conditions.

1.06 MAINTENANCE

- A. 	Provide all parts, materials, fluids, etc. necessary for maintenance and calibration purposes throughout the warranty period. Deliver all of these supplies before substantial project completion.

- 1.07  WARRANTY

- The meter shall have standard one year warranty from date of shipment and if the meter is commissioned by a factory certified technician, the warranty is extended to three years from the date of shipment.

1.08 LIFECYCLE MANAGEMENT

A.	Instrument documentation, like original calibration certificates, manuals and product status information shall be accessed via a web enabled system with a license. The instrument-specific information shall be accessed via its serial number. When services are provided by an authorized service provider the services information like subsequent field calibrations shall be archived and accessible via this web enabled system.

PART 2	PRODUCTS

2.01 MANUFACTURER

- One of the following:

- Endress+Hauser- Levelflex M FMP55

2.02 MANUFACTURED UNITS

    - The transmitter shall utilize dual technologies - guided radar and capacitance, on one rod or cable in order to measure the overall liquid level and the interface between two liquids even with an emulsion layer between the two products.

    - The transmitter housing shall have dual compartments and be available in plastic, die cast aluminum powder epoxy coating or 316L stainless steel based on the application environment.

    - The transmitter shall be available as a loop powered 2-wire device with an option for 4-wires (AC or DC powered options available).

    - The instrument shall be capable of handling process temperatures between -58 degrees F and 392 degrees F. It should also withstand process pressures of -14.5 psi to 580 psi.

    - Unit shall have ATEX, FM, CSA or IECEx approvals available as required.

    - Instrument shall work accurately in foam or turbulent surfaces.

    - Outputs for the transmitter shall be 4 to 20 mA with HART with an optional second current output. Profibus PA and Foundation Fieldbus shall be available as an option.

    - Application in safety related systems with requirements for functional safety up to SIL 2 independently assessed by TUV as per IEC 61508.

    - Rope probes for measurement will need to be installed in a stilling well and shall have a measuring range up to 33ft; Rod coax probes shall have a measuring range up to 20 ft.

- Unit shall have easy remote operation, diagnosis and measuring point documentation with the supplied operating program; optional remote display and operation shall be provided.

- The transmitter shall have local indicator with a 4-line LCD display scaled to read in engineering units of level, Interface level and volume. The local indicator shall be capable of displaying an envelope curve of the actual signal used for commissioning/troubleshooting purposes and have the capability of backing up/duplicating the instrument’s data.

- The local display will have the capability to store data, which will serve as backup for the configuration and allow the set-up data to be transferred to another transmitter.

- Complete set-up and configuration shall be possible via the 3-buttons built-in the display. No further equipment or parts shall be required for commissioning the unit.

- FDT based software shall be provided to offer optional remote method of configuration, set-up and storage of program via a computer.

- The transmitter shall have a built-in HistoROM which is capable of logging 100 events based on programmed triggers. This HistoRom will also store the configuration and set-up data for the transmitter.

- 2.03 SOURCE QUALITY CONTROL

- A Certificate of Compliance shall be available from the manufacturer if required.

- An application data sheet should be filled out with all known data, and submitted to the manufacturer to ensure proper instrument choice.

2.04 SAFETY

A.	All electrical equipment shall meet the requirements of ANSI/NFPA 70, NATIONAL ELECTRIC CODE, latest edition.

B.	All devices shall be certified for use in hazardous areas: Class 1, Div. 2, Groups B/C; temperature rating T3 (200 deg. C) if required.

C.	All devices shall be suitable for use as non-incendive devices when used with appropriate non-incendive associated equipment/devices with intrinsically safe ratings.  All devices will normally be acceptable with vendor’s approval.

D.	Electrical equipment housing shall conform to NEMA 4x/6P classification.

E.	The equipment shall be approved by a Nationally Recognized Testing Laboratory (NRTL) such as FM, UL, ETL, CSA, etc.) for the specified electrical area classification.

- F.	Electrical equipment specified as intrinsically safe shall qualify as “simple apparatus” or NRTL approved intrinsically safe equipment per ANSI/ISA-RP12.6 “Installation of Intrinsically Safe Systems for Hazardous (Classified) Locations”, latest edition.

PART 	3	EXECUTION

- 3.01 EXAMINATION

- Examine the complete set of plans, the process fluids, pressures, and temperatures and furnish instruments that are compatible with installed process condition.

- Examine the installation location for the instrument and verify that the instrument will work properly when installed.

- 3.02 INSTALLATION

- As shown on installation details and mechanical drawings.

- As recommended by the manufacturer’s installation and operation manual.

- Specific attention should be given to the following technical requirements:

    - Verify the transmitter is mounted in an appropriate location in the vessel as per the instruction manual.

- 3.03 FIELD QUALITY CONTROL

- Demonstrate the performance of all instruments to the ENGINEER before commissioning.

- ENGINEER to witness all instrument calibration verification in the field.

- Each instrument shall be tested before commissioning and the ENGINEER shall witness the response in the PLC control system and associated registers.

- Manufacturer’s Field Services:

- Manufacturers shall be capable of providing complete setup, commissioning and verification of the instrument prior to start up.

- Notify the ENGINEER in writing of any problems or discrepancies and proposed solutions.

- 3.04 ADJUSTING

- Factory calibration of all instruments shall be provided and only commissioning or set-up of parameters shall be required in the field in accordance with the manufacturer’s instructions.

- 3.05 PROTECTION

- All instruments shall be fully protected after installation and before commissioning.

- Replace any instruments damaged before commissioning:

- The ENGINEER shall be the sole party responsible for determining the corrective measures.