SECTION 40 72 76

LEVEL SWITCHES

- PART 1 -GENERAL

- A point level switch for use in hazardous areas with all international certificates. The FTL50 is useable in all industries and has functional SIL2/SIL3 safety. It offers reliable measurement value that is not affected by flow, turbulence, bubbles, foam, vibration, bulk solids content or build-up.

1.02 SUBMITTALS

- Furnish complete Product Manufacturer’s Technical Information, Operating and Maintenance

- Product Data:

  - Dimensional Drawings.

  - Materials of Construction.

  - Measurement accuracy.

  - Range and range ability.

  - Enclosure Rating.

  - Classification Rating.

  - Power.

  - Output options.

1.03 	QUALITY ASSURANCE

- Manufacture instrument facilities certified to the quality standards of ISO Standard 9001 - Quality Systems - Model for Quality Assurance in Design/Development, Production, Installation, and Servicing.

1.04 	DELIVERY, STORAGE, AND HANDLING

- Store all instruments in a dedicated structure with space conditioning to meet the recommended storage requirements provided by the Manufacturer.

- Any instruments that are not stored in strict conformance with the Manufacturer’s recommendation shall be replaced.

1.05 		PROJECT OR SITE CONDITIONS

- Provide instruments suitable for the installed site conditions including, but not limited to, material compatibility, site altitude, process and ambient temperature, and humidity conditions.

1.06 	WARRANTY

- The meter shall have standard one year warranty from date of shipment and if the meter is commissioned by a factory certified technician, the warranty is extended to three years from the date of shipment.

- 1.07 	MAINTENANCE

A.	Provide all parts, materials, fluids, etc. necessary for maintenance and calibration purposes throughout the warranty period. Deliver all of these supplies before project completion.

1.08 	LIFECYCLE MANAGEMENT

A.	Instrument documentation, like original calibration certificates, manuals and product status information, shall be accessed via a web enabled system with a license. The instrument-specific information shall be accessed via its serial number. When services are provided by an authorized service provider, the services information like subsequent field calibrations shall be archived and accessible via this web enabled system.

PART 2 –PRODUCTS

  - MANUFACTURER

- Endress+Hauser- Liquiphant FTL50/51

2.02 	MANUFACTURED UNITS

A.	Operation:  The turning fork vibrates at its resonance frequency until covered by fluid. When this occurs the resulting frequency shift activates a change of state in the unit’s electronics.

B.	Functional:  Status indication – via dual LEDs; power supply  - AC 19 to 253 V 50/60 Hz of 10 to 55 VDC with over voltage protection; output- AC 2-wire, OC PNP, AC/DC Relay, 8/16 mA, NAMUR or PFM.

C.	Physical:  Wetted parts – 316L stainless steel, Alloy C, PFA, Enamel or ECTFE (Halar) as specified; body material – powder-coated NEMA4X  aluminum housing with FM approval;

D.	Process connection –MNPT or flanged as listed in schedule; extension length – up to 115 inches for non-coated version.  Where hazardous areas are indicated, the equipment shall be rated for that area.

E.	Performance:  Millimeter precision switch point; maximum fluid viscosity – 10000 cP; minimum fluid density - .5 g/cm³

F.	Options:  Sliding sleeve for vertical adjustment of tuning fork as required.

2.03 	ACCESSORIES

A.	Weld-in adapter

B. 	Weather protection cover

C. 	Lap joint flanges

D. 	Sliding sleeves for unpressurized operation

E.	High pressure sliding sleeves

- 2.04 	SOURCE QUALITY CONTROL & CALIBRATION

- A Certificate of Compliance shall be available from the manufacturer if required.

B. 	An application data sheet should be filled out, with all known data, and submitted to the manufacturer to ensure proper instrument choice.

- 2.05 	SAFETY

- A.	All electrical equipment shall meet the requirements of ANSI/NFPA 70, NATIONAL ELECTRIC CODE, and latest addition.

- B.	All devices shall be certified for use in the following hazardous areas:

- 1.	Explosion proof: Class I, Div. 1, Groups ABCD, Temperature rating T6 (Ta= 70ºC)

- 2.	Intrinsically safe: Class I, II, III, Div. 1, Groups ABCDEF, Temperature rating T5 (Ta=70ºC)

- 3.	Non-Incendive- Class I, Div. 2, Groups ABCD, Temperature rating T5 (Ta= 70ºC)

- C.	All devices shall be suitable for use as non-incendive devices when used with appropriate non-incendive associated equipment/devices with intrinsically safe ratings and will normally be acceptable with vendor’s approval.

- D.	Electrical equipment housing shall conform to NEMA 4x classification.

- E.	Non-intrinsically safe electrical equipment shall be approved by a Nationally Recognized Testing Laboratory (NRTL) such as FM, UL, ETL, CSA, etc.) for the specified electrical area classification.

- F. 	Electrical equipment specified as intrinsically safe shall qualify as “simple apparatus” or NRTL approved intrinsically safe equipment per ANSI/ISA-RP12.6 “Installation of Intrinsically Safe Systems for Hazardous (Classified) Locations,” latest edition.

PART  3 –EXECUTION

- 3.01 	EXAMINATION

- Examine the complete set of plans, the process fluids, pressures and temperatures and furnish instruments that are compatible with installed process condition.

- Examine the installation location for the instrument and verify that the instrument will work properly when installed.

- 3.02 	INSTALLATION

- As shown on installation details and mechanical drawings.

- As recommended by the Manufacturer’s installation and operation manual.

- 3.03 	FIELD QUALITY CONTROL

- Demonstrate the performance of all instruments to the ENGINEER before commissioning.

- ENGINEER to witness all instrument calibration verification in the field.

- Each instrument shall be tested before commissioning and the ENGINEER shall witness the response in the PLC control system and associated registers.

- Manufacturer’s Field Services:

- Manufacturers’ representative shall verify installation of all installed flow tubes and transmitters.

- Notify the ENGINEER in writing of any problems or discrepancies and proposed solutions.

- 3.04 	ADJUSTING

- Verify factory calibration of all instruments in accordance with the Manufacturer’s instructions.

- 3.05 	PROTECTION

- All instruments shall be fully protected after installation and before commissioning.  Replace any instruments damaged before commissioning:

      - The ENGINEER shall be the sole party responsible for determining the corrective measures.