SECTION 40 78 26

Paperless Recorder and Display Measuring System

- PART 1- GENERAL

- Complete recording and visualization of all process sequences. The Memograph M RSG40 has a wide range of functionality, modular construction and an intuitive operator concept.

B 1.02 SUBMITTALS

- Furnish complete Product Data, Shop Drawings, Test Reports, Operating Manuals, Record Drawings, Manufacturer’s certifications, Manufacturer’s Field Reports

- Product Data:

  - Dimensional Drawings.

  - Materials of Construction.

  - Range and range ability.

  - Classification Rating.

  - Power:

    - Voltage.

  - Output options.

1.03 QUALITY ASSURANCE

- Manufacture instruments facilities certified to the quality standards of ISO Standard 9001 - Quality Systems - Model for Quality Assurance in Design/Development, Production, Installation, and Servicing.

1.04 DELIVERY, STORAGE, AND HANDLING

- Store all instruments in a dedicated structure with space conditioning to meet the recommended storage requirements provided by the Manufacturer.

- Any instruments that are not stored in strict conformance with the Manufacturer’s recommendation shall be replaced.

1.05 PROJECT OR SITE CONDITIONS

- Provide instruments suitable for the installed site conditions including, but not limited to, material compatibility, site altitude, process and ambient temperature, and humidity conditions.

- 1.06 WARRANTY

- The meter shall have standard one year warranty from date of shipment and if the meter is commissioned by a factory certified technician, the warranty is extended to three years from the date of shipment.

1.07 MAINTENANCE

- A. 	Provide all parts, materials, fluids, etc. necessary for maintenance and calibration purposes throughout the warranty period. Deliver all of these supplies before project substantial completion.

1.08 LIFECYCLE MANAGEMENT

A.	Instrument documentation, like original calibration certificates, manuals and product status information shall be accessed via a web enabled system with a license. The instrument-specific information shall be accessed via its serial number. When services are provided by an authorized service provider the services information like subsequent field calibrations shall be archived and accessible via this web enabled system.

PART 2 -PRODUCTS

  - MANUFACTURER

- Endress+Hauser- Memograph M RSG40

2.02 MANUFACTURED UNITS

A.	The unit shall have a 7" TFT display as onsite display for optimum readability.

B.	The recorder shall have a 100 msec scan rate for all channels, high-speed memory cycle 100 msec for up to 8 channels.

C.	The unit shall have a security package with person-specific access authorization and electronic signature (FDA 21 CFR 11).

D.	The unit shall have easy retrofitting to up to 20 universal inputs and 14 digital inputs or 12 relays.

E.	Preformatted screen display, such as horizontal or vertical curves, bar graphs, instrument display, circular chart or digital display.

F.	The unit shall have an integrated Web server, fieldbus (Profibus, Modbus), common standard protocols and interfaces such as USB, TCP/IP, OPC and Ethernet are supported.

G.	Installation depth shall be 158 mm, plastic front IP65, NEMA4; Operating via external USB keyboard, printout via USB printer

  - Accessories

- Retrofit kit desktop version

- RS232/485 adapter set, DIN rail 230VAC, with galv. Isolation for PC/modem

- Memory card SD 512 MB, industrial grade or SD 256 MB, industrial grade

2.04 Source Quality Control and Calibration

A.	Provide ISA data sheet ISA-TR20.00.01. Use the latest revision of form 20F2321. Complete the form with all known data, and dash out the inapplicable fields. Incomplete data sheets submitted will be result in a rejected submittal.

B.	Provide complete documentation covering the traceability of all calibration instruments.

- 2.05 Safety

A.	All electrical equipment shall meet the requirements of ANSI/NFPA 70, NATIONAL ELECTRIC CODE, latest addition.

B.	All devices shall be certified for use in hazardous areas: Class 1, Div. 2, Groups B/C; temperature rating T3 (200 deg. C)

C.	All devices shall be suitable for use as non-incendive devices when used with appropriate non-incendive associated equipment/ Devices with intrinsically safe ratings will normally be acceptable with vendor’s approval.

D.	Electrical equipment housing shall conform to NEMA 4x classification.

E.	Non-intrinsically safe electrical equipment shall be approved by a Nationally Recognized Testing Laboratory (NRTL) such as FM, UL, ETL, CSA, etc.) for the specified electrical area classification.

- F.	Electrical equipment specified as intrinsically safe shall qualify as “simple apparatus” or NTRL approved intrinsically safe equipment per ANSI/ISA-RP12.6 “Installation of Intrinsically Safe Systems for Hazardous (Classified) Locations”, latest edition.

PART 	3- EXECUTION

- 3.01 EXAMINATION

- Examine the complete set of plans, the process fluids, pressures, and temperatures and furnish instruments that are compatible with installed process condition.

- Examine the installation location for the instrument and verify that the instrument will work properly when installed.

- 3.02 INSTALLATION

- As shown on installation details and mechanical Drawings.

- As recommended by the manufacturer’s installation and operation manual.

- 3.03 FIELD QUALITY CONTROL

- Demonstrate the performance of all instruments to the ENGINEER before commissioning.

- ENGINEER to witness all instrument calibration verification in the field.

- Each instrument shall be tested before commissioning and the ENGINEER shall witness the response in the PLC control system and associated registers.

- Manufacturer’s Field Services:

- Notify the ENGINEER in writing of any problems or discrepancies and proposed solutions.

- 3.04 ADJUSTING

- Verify factory calibration of all instruments in accordance with the Manufacturer’s instructions.

- 3.05 PROTECTION

- All instruments shall be fully protected after installation and before commissioning. Replace any instruments damaged before commissioning:

      - The ENGINEER shall be the sole party responsible for determining the corrective measures.